By:

Heidi Benzonelli

Vernon Bevan

Vyomini Pandya

Robert Tingleff

Table of Contents

Executive Summary	i

1. Site Loads	i

2. Phase I - Ranch house	i

3. Phase I - Long house	iii

4. Phase II – Micro-hydro integration	iv

1.	Introduction	1

2.	Background	1

3.	Design	3

3.1.	Phase I	7

3.2.	Phase II	11

4.	Economic Analysis	18

4.1.	Phase I	18

4.2.	Phase II	23

5.	Recommendations	24

6.	References	24

7.	Appendices	25

A.	Available Data	25

Solar Insolation	25

Micro-hydro	25

B.	Load Analysis	26

C.	Sizing the System	32

D.	Micro-hydro calculations	37

E.	Breakdown of Costs	39

F.	Sources for prices	41

List of Tables

Table 1: Insolation data for Rock Creek Ranch in kW-hrs/m2-day.	2

Table 2: Estimated load for Rock Creek Ranch.	2

Table 3:  Battery bank sizing for summer and winter anticipated loads.	3

Table 4: Phase I Design configuration for Rock Creek Ranch.	8

Table 5: Associated values used to specify Micro-hydro system design	12

Table 6: Micro-hydro Generator Specifications (HP, 2006)	13

Table 7: Summary of additional micro-hydro System components.	14

Table 8: Gallons of gasoline required to meet loads at each location.	19

Table 9: Energy costs for alternatives	19

Table 10: Alternative 1 life cycle costs	19

Table 11: Alternative 2 life cycle costs	21

Table 12: Sensitvity on life cycle costs based on escalation rate	23

Table 13: Life cycle cost for Phase II (micro-hydro)	23

List of Figures

Figure 1:  Ranch house/Cabin loads compared to PV array output for 10 panels.	4

Figure 2: Ranch house/Cabin loads compared to PV array output for 12 panels.	4

Figure 3: Long house loads compared to PV array output for 6 panels.	5

Figure 4:  Long house loads compared to PV array output for 8 panels.	6

Figure 5: Phase I Schematic for the Ranch House/Caretaker's Cabin	9

Figure 6: Solar system at long house	10

Figure 7: 30 Year Average daily precipitation data for the Gasquet Ranger Station (GRS, 2006).	11

Figure 8: Winter flows at Micro-hydro site.	12

Figure 9: Schematic of Phase II Ranch House	15

Figure 10: Schematic Phase II Long House	16

Figure 11: Location of system elements at Rock Creek Ranch site	17

# Executive Summary

This summary contains the key recommendations of the Survey Experts group to the Smith River Alliance (SRA) regarding the design of an off-grid energy system to be installed at the Rock Creek Ranch (RCR).  Our design consists of two phases.  In the first phase, photovoltaic arrays are installed at two sites at RCR – the orchard site near the main house (the ranch house), and the roof of the secondary house (the long house).  Each site will have its own inverter and battery bank.  In the second phase, a micro-hydro system is installed based on outflow from a culvert crossing under the road above RCR, and power from it is delivered to both the ranch house and the long house.

## 1. Site Loads

The assumptions in Table ES-1 were used in sizing system components.  The table shows the assumed average daily load for summer and winter at each site, as well as maximum possible instantaneous loads (the total connected Watts) at each site.

Table ES-1: These assumptions were used in sizing the solar system.

| Load Assumptions |
| --- |
|  |  | Summer | Winter |
| Ranch house | AC (W-hrs/day) | 1993 | 1402 |
|  | DC (W-hrs/day) | 1197 | 552 |
|  | AC (Connected W) | 3821 | 3821 |
|  | DC (Connected W) | 66 | 66 |
| Long house | AC (W-hrs/day) | 1263 | 754 |
|  | DC (W-hrs/day) | 159 | 0 |
|  | AC (Connected W) | 544 | 544 |
|  | DC (Connected W) | 25 | 0 |
| Caretaker's Cabin | AC (W-hrs/day) | 499 | 607 |
|  | DC (W-hrs/day) | 0 | 0 |
|  | AC (Connected W) | 148 | 148 |
|  | DC (Connected W) | 0 | 0 |

## 2. Phase I - Ranch house

We sited the PV array in the orchard, 340 feet from the ranch house.  The PV panels will be mounted on an adjustable pole mount.  We assumed that they will be adjusted monthly; less frequent adjustments would make little difference in the calculations.  We sized the battery bank to provide for five days without charging at the assumed winter-time loads, with a maximum battery state of discharge of 60%.

Based on life cycle costs, we recommend twelve 115W PV panels at this site, two more than the number already purchased by the SRA.  We also consider ten panels to be a viable option at this site.  The ten panel design has the advantage of lower initial costs.  The major components for Phase I at the ranch house are shown in Table ES-2.  We assumed that initially the existing Honda generator would be used to charge the batteries when there is insufficient solar resource.

Table ES-2: Major ranch house system components are summarized.

| Inverter | Trace SW 2512 |
| --- | --- |
| Batteries | 10 Interstate UL-16 6V deep cycle |
| PV Panels | 12 Evergreen EC-115 |
| Charge Controllers | 2 Outback MX-60 |
| Generator | Honda EM5000S |
| Wire – panels to controllers | 2 sets AWG 8 plus ground wire |

Initial costs for the major components at the ranch house are summarized in Table ES-3 for the twelve panel option.  Costs for items such as installation, disconnects, smaller wire runs, overcurrent protection devices, and circuit breaker panels are very rough estimates.  Capital costs are only for required new items.

Table ES-3: Initial costs of major new ranch house system components are shown.

| Item | Description | Quantity | Costs Each ($) | Capital Cost ($) | Life Time (yrs) |
| --- | --- | --- | --- | --- | --- |
| PV Panels | EG-115 | 12 (2 new) | 618.00 | 1236.00 | 30 |
| Copper wires | 340 ft AWG 8 | 4 | 0.73 | 992.80 | 30 |
| Other wires | Ground, misc |  |  | 346.78 | 30 |
| Charge Controller | Outback MX-60 | 2 (1 new) | 649.00 | 649.00 | 10 |
| Batteries | Interstate UL-16 | 10 | 199.95 | 1999.50 | 6-10 years |
| Generator | Honda EM5000S | 1 | 2681.95 | 0 | 15 |
| Inverter | Trace SW 2512 | 1 | 1299.00 | 0 | 15 |
| Mounting rack | Pole mount | 1 | 840 | 840 | 30 |
| Disconnect | Outback PS2DC-175 | 1 | 375 | 375 | 30 |
| Miscellaneous | Fuses, AC/DC panels, misc |  | 500 | 500 | 30 |
| Trench | Orchard to house |  | 500 | 500 | 30 |
| Installation | Labor |  | 500 | 500 |  |
| Total |  |  |  | $7898.30 |  |

Life cycle costs for two options for the standalone ranch house system are shown in Table ES-4.  The life cycle analysis is for a period of 30 years.  We assumed a discount rate of 4%.  This table shows the cost of gasoline required to make up the deficit during the winter months.  Based on specifications in the generator manual, and on information provided by the SRA, we assumed a generator efficiency of about 10% in converting gasoline to electricity.  The life cycle cost analysis shows higher initial costs for the 12 panel option, but lower life cycle costs.  We assumed that the price of gasoline would increase at the historical rate of the past 10 years - 1.7% greater than the general inflation rate.  The 10 panel option has higher initial costs for wires due to 60 Volt transmission compared with 72 Volts for 12 panels.

Table ES-4: Present values of 30 year life cycle costs are shown for the ranch house.

| Option | Initial cost | Energy costs | Operation & Maintenance | Capital replacement | Salvage value | Total life cycle cost |
| --- | --- | --- | --- | --- | --- | --- |
| 10 panels | $7073 | $9922 | $1729 | $7541 | $810 | $25,455 |
| 12 panels | $7898 | $7868 | $1729 | $7541 | $795 | $24,128 |

We encountered two major issues at the ranch house site – long wire runs and the limitations of a 12V battery bank and inverter.  At 12V, the current from more than 800W input from PV panels would be too great for a single 60A charge controller.  We considered changing the system voltage to 48V, which would have required the purchase of a new inverter.  Based on capital costs, we selected the 12V option, which requires the purchase of an additional charge controller, as well as two sets of wires from the PV panels to the controllers.

## 3. Phase I - Long house

At the second site at RCR, we selected eight 75W PV panels, located on the north end of the house.  This would require the purchase of two new 75W panels.  In this case, the life cycle cost is higher with eight panels.  The reduced costs for gasoline were not sufficient to make up for the increased capital expense of the two additional panels.  We recommend eight panels based on the possibility of new loads at this site.  We assumed that the panels were permanently tilted to latitude minus 15°. We recommend four 6V, 375Amp-hr batteries at this site to achieve five days without charging during the winter.  For the initial set of batteries, we recommend using the existing six 6V batteries.  The major components at the long house site are summarized in Table ES-5.

Table ES-5: Major long house system components are summarized.

| Inverter | Trace SW 1512 |
| --- | --- |
| Batteries | 6 Interstate UL-16 |
| PV Panels | 6 existing 75W panels; 2 additional 75W panels |
| Charge controller | 1 Xantrex C-60 |

Initial costs for the major components at the long house are summarized in Table ES-6 for the eight panel option.  The capital costs only include the new items.  Costs for items such as overcurrent protection, installation, and an AC circuit breaker panel are rough estimates.  Life cycle costs for the long house system are summarized in Table ES-7.

Table ES-6: Initial costs of new long house system components are shown.

| Item | Description | Quantity | Costs Each ($) | Capital Cost ($) | Life Time (yrs) |
| --- | --- | --- | --- | --- | --- |
| PV Panels | Sharp 80V | 2 new | 479.16 | 958.32 | 30 |
| Charge Controller | Xantrex C-60 | 1 | 167.16 | 167.16 | 10 |
| Batteries | Interstate UL-16 | 6 | 199.95 | 0 | 6-10 years |
| Generator | Honda EM5000S | 1 | 2681.95 | 0 | 15 |
| Inverter | Trace SW 1512 | 1 | 799.00 | 799.00 | 15 |
| Mounting rack | Roof mount | 1 | 258.00 | 258.00 | 30 |
| Disconnect | 100 amp | 1 | 325.00 | 325.00 | 30 |
| Wires | All |  | 69.56 | 69.56 | 30 |
| Miscellaneous | Fuses, AC panel |  | 350.00 | 350.00 | 30 |
| Installation | Labor |  | 500.00 | 500.00 |  |
| Total |  |  |  | $3,442.25 |  |

Table ES-7: Present values of 30 year life cycle costs are shown for the long house.

| Option | Initial cost | Energy costs | Operation & Maintenance | Capital replacement | Salvage value | Total life cycle cost |
| --- | --- | --- | --- | --- | --- | --- |
| 6 panels | $2444 | $2127 | $1729 | $3392 | $109 | $9583 |
| 8 panels | $3402 | $1551 | $1729 | $3392 | $168 | $9906 |

## 4. Phase II – Micro-hydro integration

The RCR has very good potential for micro-hydro power.  SRA members have estimated the flow at a culvert near the property at greater than 100 gallons per minute for most of the winter.  We measured the head at this site at 72 ft., leading to an estimate of 480W from the generator.  Delivering the power to both houses will require the installation of 315 ft. of wire from the turbine powerhouse to the long house, and the installation of 793 ft. of new wire from the turbine to the ranch house.  To minimize wire costs, we selected a 600W AC turbine/generator set that outputs 120V wild AC.  A rectifier and transformer will be required at each site.  At each site, a diversion charge controller will divert power to a load such as a water heater, space heater, or hot tub when the batteries are fully charged.  The major components of the micro-hydro system are summarized in Table ES-8.

Table ES-8: Additional micro-hydro system components are summarized.

| Turbine and generator | Harris HV 600 |
| --- | --- |
| Pipe | 220 ft. schedule 40 3” PVC |
| Transformer and rectifier | Included with HV 600 (120V) |
| Intake/sedimentation basin | Engineering & construction needed |

Capital costs for the main micro-hydro system components are shown in Table ES-9.  Costs for the trench, intake, powerhouse, and construction are very rough estimates.

Table ES-9: Initial costs for major micro-hydro components are shown.

| Item | Description | Quantity | Costs Each ($) | Capital Cost ($) | Life Time (yrs) |
| --- | --- | --- | --- | --- | --- |
| Turbine and generator | Hi-power Hydro 600W 120V AC | 1 | 2500.00 | 2500.00 | 15 |
| Pipeline | 3” Schedule 40 PVC | 220 ft. | 21.55/9 ft. | 538.75 | 30 |
| Rectifier/transformer | Hi-power Hydro | 1 extra | 50 | 50 | 15 |
| Wire | Copper AWG 6 | 2 @793 ft. | 0.97/ ft. | 1538.42 | 30 |
| Wire | Copper AWG 10 | 2 @315 ft. | 0.38/ ft. | 239.40 | 30 |
| Trench | Turbine to long house | 315 ft. | 500 | 500 | 30 |
| Powerhouse |  |  | 500 | 500 |  |
| Intake | Flume & basin |  | 2000 | 2000 |  |
| Construction | Intake & other |  | 2000 | 2000 |  |
| Total |  |  |  | $9867 |  |

Life cycle costs for the complete system after installation of the micro-hydro system are shown in Table ES-10.  We assumed that the gas generator would only be needed to make up the deficit in September, October, and half of November.  With the micro-hydro system replacing most of the gasoline, the life cycle cost is lower with the smaller number of PV panels.

Table ES-10: Present values of 30 year life cycle costs are shown assuming installation of both the micro-hydro system and the PV installations at both houses.

| Option | Initial cost | Energy costs | Operation & Maintenance | Capital replacement | Salvage value | Total life cycle cost |
| --- | --- | --- | --- | --- | --- | --- |
| 16 panels | $19,874 | $2413 | $5187 | $12,396 | $1027 | $40,897 |
| 20 panels | $21,543 | $1311 | $5187 | $12,396 | $1071 | $41,508 |

A benefit of the renewable energy systems not included in these numbers is the value of the fuel displaced when “excess” solar energy and micro-hydro energy are used for water or space heating.

The locations of the renewable energy system components are shown in Figure ES-1.

Figure ES-1: Renewable energy system components are shown at the Rock Creek site.

# Introduction

Rock Creek Ranch is owned by the Smith River Alliance.  The Smith River Alliance (SRA) is an organization founded in 1980 to restore and protect natural resources in the Smith River watershed. Rock Creek Ranch is located 8 miles south of the confluence of the Middle and South forks of Smith River. The ranch covers 15 acres bordering the Smith River. Existing facilities at Rock Creek Ranch include a ranch house, occupied by a caretaker, and the long house which provides minimal amenities for overnight guests.  No public utilities are available at the site and electrical power is currently provided by a battery bank and gasoline-powered generator.

Ranch Creek Ranch is used by the SRA to provide a location for summer retreats, youth camps, and educational workshops. The SRA anticipates expanding activities at Rock Creek Ranch, especially during the summer.  The expansion plans include construction of a caretaker’s cabin, which would free up more space in the ranch house for overnight guests.

To meet future electrical power demands, the SRA has requested that we design a renewable energy system for Rock Creek Ranch. The renewable energy system should be primarily based on photovoltaics.  However, there is a seasonal stream on site which may provide an option for micro-hydro power.  The design options we present here are decentralized.  Each facility will have its own power generation and storage capabilities.  A benefit of this design is that the renewable energy system can be built in phases congruent with the amount of capital available at a given time.

# Background

In order to design a stand alone PV system, we began by assessing present loads and possible sites for PV arrays.  Next we performed a load analysis based on observations and communication with residents of Rock Creek Ranch.  To complete our loads assessment it was necessary for us to make certain assumptions.  We designed for what we thought the average daily load might be as opposed to the maximum load, which included all appliances running simultaneously.  We also made assumptions of how summer versus winter use of the facility would affect the electrical loads.  These assumptions are reflected in the sizing spreadsheet in Appendix C.

The first step in designing a photovoltaic system is determining the potential locations for PV arrays.  One of our initial assumptions was that caretaker’s cabin would be built in close proximity to the existing ranch house.  Due to their close proximity, we decided that power will be provided to the Ranch House and Caretaker’s Cabin by the same PV array and battery bank.

In regard to the long house, determining the location of the PV array was straightforward.  Based upon solar pathfinder analysis as well as ease of installation, we selected the roof of the long house.  Determining the location of the array for the ranch house/caretaker’s cabin was also tightly constrained.  The roof of either structure was ruled out due to a high degree of shading.  The only feasible location was the orchard, which is located about 300 feet away from the ranch house.

Another of our initial assumptions was that solar insolation collected at the Gasquet airport was characteristic of conditions at Rock Creek Ranch. Once we collected the appropriate solar data, they were integrated into PV array sitting considerations and shading analysis.  The result of this was an estimate for the amount of solar energy at each site that would be available for the PV array (Table 1).

Table 1: Insolation data for Rock Creek Ranch in kW-hrs/m2-day.

|  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Insolation data from Gasquet, CA on a horizontal surface | 0.76 | 1.86 | 2.84 | 4.04 | 5.60 | 6.90 | 7.19 | 6.00 | 4.74 | 2.60 | 1.12 | 0.54 |
| Insolation on surface elevated to (latitude-declination) monthly | 0.65 | 2.48 | 3.24 | 4.16 | 5.52 | 6.69 | 7.02 | 6.13 | 5.50 | 3.54 | 1.03 | 0.44 |
| Solar availability at orchard site – fraction available after shading | 29% | 90% | 77% | 77% | 77% | 93% | 94% | 88% | 87% | 86% | 54% | 17% |
| Available insolation in orchard on tilted surface (after shading) | 0.19 | 2.23 | 2.49 | 3.20 | 4.25 | 6.22 | 6.60 | 5.39 | 4.79 | 3.04 | 0.56 | 0.07 |
| Available insolation on surface permanently tilted to (latitude-15°) | 0.76 | 2.35 | 3.23 | 4.20 | 5.45 | 6.47 | 6.86 | 6.15 | 5.47 | 3.33 | 1.15 | 0.53 |
| Solar availability at long house roof site – fraction after shading | 72% | 83% | 78% | 77% | 78% | 81% | 80% | 82% | 81% | 88% | 72% | 69% |
| Available insolation on tilted surface (after shading) | 0.52 | 2.05 | 2.53 | 3.11 | 3.94 | 4.75 | 5.01 | 4.78 | 4.44 | 3.09 | 0.81 | 0.35 |

After assessing site characteristics and solar pathfinder data we conducted a load analysis to determine the power demand at Rock Creek Ranch.  The analysis was performed for the long house, ranch house and caretaker’s cabin.  The load analysis for the long house and ranch house contain estimates for AC as well as DC loads.  The DC loads consist of a Sunfrost DC refrigerator and freezer, which functions as a refrigerator.  The analysis was subjective as assumptions were made regarding future energy use based upon the expected increased activity at Rock Creek Ranch. Ultimately, the Engineering 475 class agreed on a common load analysis to provide a common starting point (Table 2).

Table 2: Estimated load for Rock Creek Ranch.

| Location | Type of Load | Summer | Winter |
| --- | --- | --- | --- |
| Ranch House | AC (W-hrs/day) | 1993 | 1402 |
|  | DC (W-hrs/day) | 1197 | 552 |
| Long House | AC (W-hrs/day) | 1263 | 754 |
|  | DC (W-hrs/day) | 159 | 0 |
| Caretaker’s Cabin | AC (W-hrs/day) | 499 | 607 |
|  | DC (W-hrs/day) | 0 | 0 |

Finally, as there is a seasonal stream on site, the potential exists for micro-hydro power generation.  Fortunately, the stream flows during the winter when solar insolation is insufficient to meet the power demand.  Thus, micro-hydro is a design option to be considered.

# Design

The assumptions and decisions made in the previous section provided the basis for designing the system.  The sizing calculations for all components are included in Appendix C.  First, we sized the inverter.  At the ranch house and caretaker’s cabin, the total connected AC Watts is 3969W.  This exceeds the maximum continuous output possible with the existing Trace 2500W inverter.  We chose to use the existing inverter, and to advise the SRA that they may need to restrict access to appliances such as the vacuum, washer, and dryer when guests are present.  At the long house, the maximum possible instantaneous load is 544 W.  We selected a Xantrex 1512 inverter for the long house.

We also considered the possibility of running the long house on DC power.  In this case, the SRA would not need to purchase an inverter and all loads would need to be DC.  This option would reduce initial cost.  However, it would reduce flexibility if the number and type of loads were to increase.

The Smith River Alliance owns six 12 volt interstate UL-16 batteries which are being used at the ranch house.  To reduce costs, we anticipate that these batteries will be used in the new energy system.  Therefore, we used these batteries in the sizing analysis.  The battery banks were sized for both winter and summer loads for comparison.  The battery banks at both locations were sized for 2 days of autonomy with summer loads, and 5 days of autonomy with winter loads.  At both locations the depth of discharge was assumed to be 60%.  In addition, the battery banks at both locations were designed for 12 volt.  The reasons for this were that SRA already owns a Trace 12 Volt inverter as well as two 12 volt, DC Sunfrost refrigerators.  The results of battery sizing are included in Table 3.

Table 3:  Battery bank sizing for summer and winter anticipated loads.

| Location | Season | Batteries in Series | Batteries in Parallel | Total Batteries |
| --- | --- | --- | --- | --- |
| Ranch House/ Caretaker's Cabin | Summer | 2.00 | 2.85 | 5.70 |
| Ranch House/ Caretaker's Cabin | Winter | 2.00 | 4.98 | 9.96 |
| Long House | Summer | 2.00 | 1.11 | 2.23 |
| Long House | Winter | 2.00 | 1.49 | 2.97 |

Based on the sizing calculations, we specified ten 6V, 375 Amp-hr batteries for the ranch house, and 4 similar batteries for the long house.  Initially we expect that the existing 6 batteries at the ranch house would be used at the long house.

Our sizing calculations for the PV array at the ranch house/caretaker’s cabin were based on Evergreen EC-115 PV modules.  The SRA already owns ten panels which will be incorporated into the design.  For the long house, array sizing was based upon 75W panels.  The SRA already owns four Siemens SP75 modules (75 W) and 2 BP 380V panels (80 W).  We specified an additional two Sharp 80W panels.  To size the PV array, summer and winter loads were compared against insolation data for a number of months.

We graphed expected loads at both locations against the PV array output that would be delivered to the loads.  We did this for 10 and 12 panels at the ranch house/caretaker’s cabin and for 6 and 8 panels at the long house.  We calculated PV output after shading and assumed a 95% efficient controller, 90% efficient inverter, 80% efficient batteries, and 95% efficient wire runs (Figure 1, Figure 2, Figure 3, and Figure 4).  In addition, we derated PV output by 12% according to the manufacturers’ specifications for voltage drop with temperature.

Figure 1:  Ranch house/Cabin loads compared to PV array output for 10 panels.

Figure 2: Ranch house/Cabin loads compared to PV array output for 12 panels.

Figure 1 indicates a tight fit between power demand and generation. Very little extra power is produced.  In contrast, Figure 2 indicates power will be produced that will be diverted to loads such as water or space heating.  In both cases there is a power generation deficit during part of the year.  For 10 panels this occurs from September through April.  For the 12 panel option the deficit occurs from November through March.

Another consideration in regards to the PV array for the ranch house/cabin is output voltage.  The PV array site is located 340 ft from the battery bank.  A high voltage output from the array would minimize wire size and costs.  For a 10 panel array (2 parallel strings of 5) the nominal voltage is 60 volts whereas for a 12 panel array (2 parallel strings of 6) it is 72 volts.  These considerations will affect other aspects of system sizing.

Figure 3: Long house loads compared to PV array output for 6 panels.

Figure 4:  Long house loads compared to PV array output for 8 panels.

The situation is similar for the long house.  Figure 3 illustrates a close correlation between power demand and generation.  In contrast, Figure 4 indicates excess power is being produced during the summer.  As before, there is a power generation deficit for both scenarios during certain times of the year.  There is approximately a 6 month deficit for the 6 panel scenario and 3 month deficit for the 8 panel scenario.

The decision to be made for both locations in regard to PV configuration comes down to a few issues:

1.  How much is the SRA prepared to supplement power production with a generator?

2.  How good were the load estimates in regards to future usage and growth?

3.  How important are initial costs compared with life cycle costs?

4.  How close are the solar insolation and PV output numbers?

The answer to these questions will help determine the final PV array configuration.

Our next design consideration was the charge controller.  The SRA owns an Outback MX-60, which is already in use at the ranch house.  To avoid buying new components we decided to base our design options on the MX-60 if possible.  However, for the ranch house/caretaker’s cabin there are some considerations to be evaluated.

For both the 10 panel and 12 panel scenarios, the current output from the MX-60 will exceed specifications.  The MX-60 will output 12 volts at a maximum of 60 amps.  A 10 panel PV array can produce 1150W.  The resulting output from the charge controller would be 96 amps at 12 volts.  A 12 panel array could generate 1380W, and the output from the charge controller would be 115 amps at 12 volts.

We considered two possible solutions to overcome this obstacle: sizing the battery bank for 12 volts and sizing the battery bank for 48 volts.  Sizing the battery bank for 48 volts would involve outputting 48 volts from the charge controller, purchasing a 48 volt inverter and using the existing Trace 2512 inverter for the long house.  It would also involve converting the Sunfrost refrigerators to AC.  A benefit of the 48 volt option would be a single wire run of 340 ft from the PV array to the ranch house.

The 12 volt option would involve purchasing another MX-60 and require 2 wire runs from the PV array.  Each parallel string of six modules from the PV array would be wired to its own charge controller.  It would still be possible to use the Trace 2512 as well as the Sunfrost refrigerator.  However, it would be necessary to purchase a new 1500 Watt inverter for the long house.

At the longhouse, a maximum power point charge controller does not provide a great benefit in regards to maximizing the power output from the PV array.  This is because the array at the longhouse is a smaller array made up of three different types of panels with different optimal operating voltages.  In this case we recommend the Xantrex C-60 charge controller.

The final component to be designed was the wire sizing.  Sizing wire for the ranch house was problematic due to the wire run of 340 feet from the PV array in the orchard to the battery bank at the ranch house.  This long distance dramatically increases the cost of the wire.  One reason we decided on PV array outputs of 60 volts and 72 volts was to minimize wire size and therefore cost.  In addition, for this run, we considered aluminum instead of copper to further reduce cost.  However, aluminum wires are not favorable for a humid environment. All wire sizes for the ranch house are designed for copper.  We sized the long house wiring for both a 6 and an 8 panel array.  All wires at the long house were sized for copper.  The wire sizing worksheets for both locations are included in Appendix C.

## Phase I

Phase I of the design consists of stand alone photovoltaic systems for the long house and the ranch house/caretaker’s cabin.  In determining the final design, we considered the design objectives, assumptions and constraints, as well as economic calculations.

Phase I for the ranch house/caretaker’s cabin consists of a 12 panel, 72 volt PV array (2 parallel strings of 6).  Each parallel string is connected to an Outback MX-60 charge controller.  The charge controllers are connected in parallel on the battery side.  The battery bank consists of 10 interstate UL-16 batteries configured for 12 volt and the inverter is a Trace 2512.

For the long house, Phase I consists of an 8 panel, 24 volt PV array (4 parallel strings of 2).  The PV array is connected to a Xantrex C-60 charge controller. The battery bank is made up of 6 Interstate UL-16 batteries wired to provide 12 volts to a Trace 1512 inverter.

The components for each location are summarized in Table 4 and schematics for the ranch house /caretaker’s cabin and the long house are illustrated in Figure 6 and Figure 7 respectively.

Table 4: Phase I Design configuration for Rock Creek Ranch.

| Component | Ranch House/Cabin | Long house |
| --- | --- | --- |
| PV Array | 12 panels, 72 volts (2 parallel strings of 6) | 8 panels, 24 volts (4 parallel strings of 2) |
| Charge Controller | 2 Outback MX-60’s | 1 Xantrex C-60 |
| Batteries | 10 Interstate UL-16’s | 6 Interstate UL-16’s |
| Inverter | Trace 2512 | Trace 1512 |

Figure 5: Phase I Schematic for the Ranch House/Caretaker's Cabin

Figure 6: Solar system at long house

## Phase II

Phase I employs photovoltaics to supply the energy demand of the ranch from April to September.  Phase I depends on a generator to meet winter energy demands.  Because of the proximity to a culvert passing under the main road and draining through the RCR property, implementation of a micro-hydro generation facility is a viable alternative to petroleum powered generation.  Phase II incorporates the use of micro-hydro to meet these demands.

The two main components necessary to employ micro-hydro are elevation gradient and flow.  This site possesses both.

Altitude Gradient (drop)

A field level was used to measure the altitude change between the lip of the culvert and the landing where the micro-hydro power house is proposed. A series of backshots and foreshots were added and subtracted to arrive at an elevation difference of 71.91 feet (Appendix A).

Flow

According to a local resident who employs micro-hydro at his nearby home, the culvert at RCR flows from mid November through April.  Once it starts raining, it takes about 3 days for the cracks and interstices in the surrounding mountainous area to become saturated; once this has occurred, surface water flows through the culvert. Precipitation in the area is steady through the winter months (Figure 7).

Figure 7: 30 Year Average daily precipitation data for the Gasquet Ranger Station (GRS, 2006).

An average value for flow is based on interviews with both the caretaker and the neighbor.  Although greater flow rates are often present, the catchment system should be designed to deliver 100 GPM to the powerhouse (Figure 9).

Figure 8: Winter flows at Micro-hydro site.

Power Available/Delivered

The gross power is derived from the potential energy embodied in the falling water over time. For this site, 100GPM and 72 feet drop (less 3 feet for the intake system) are assumed. Sizing calculations for the micro-hydro system are displayed in the Appendix D.  Maximum velocity is calculated and used to find the minimum diameter pipe. It is imperative in micro-hydro systems that the pipe not be undersized.

Maximum pressure is calculated using the drop and the specific weight of water and that value is used to determine the specific pipe size for the application. The friction losses for the associated pipe and components are calculated (OSE, 2006) and used in the potential energy equation along with efficiency of the generation to get the net power available from the micro-hydro generator

(Table 5).

Table 5: Associated values used to specify Micro-hydro system design

| Drop | 69 feet |
| --- | --- |
| Flow | 100 GPM |
| Gross Power | 1301.51 Watts |
| Maximum Velocity | 20.31 m/s |
| Minimum Pipe area | 4.66 cm2 |
| Minimum Pipe diameter | 2.44 cm |
| Maximum Pressure | 29.9 psi |
| Pipe Size Sched 40 PVC | 3 inch |
| Head loss Pipe | 4.75 ft |
| Head loss Elbows | 0.26 ft |
| Head loss Gate Valve | 0.37 ft |
| Efficiency | 0.4 |
| Net Power | 480 Watts |

The calculated net power is 480 W, which will produce approximately 12 kW-hr/day.  One quarter of this amount, 3kW-h/day, is sufficient to meet all electric loads at both sites during the winter.  The remaining power, 9kWh/day, is sufficient to heat 45 gallons of water per day from 55°F to 120°F with an electric hot water heater (WSU, 2003).

Micro-hydro System Description

We selected a 600W HV generator mounted in Harris housing with a brushless permanent magnet alternator and a bronze Harris Pelton wheel.  This system is suggested for flows from 10 to 600 gpm.  At 300W, efficiency is 60%.  This system outputs 120V wild AC, and includes rectifier and transformer to reduce the voltage to 12V.

Table 6: Micro-hydro Generator Specifications (HP, 2006)

| Model | Max Power | Flow Rate @ 50psi | Transmission Voltage | Battery Voltage | Nozzles | Wheel |
| --- | --- | --- | --- | --- | --- | --- |
| HV 600 | 600 W | 50gpm | 120 VAC | 12 V | 2 | Pelton |

The system selected was specified to run with an efficiency of 60 percent for a pressure of 50 psi (Table 6).  However, for the location, the maximum pressure was calculated to be 31 psi, so the lower value of 40% for efficiency is probably safe and may even be a slight overestimate.

The long house and the ranch house will receive power from the micro-hydro powerhouse via 2 sets of wires: 1 set is estimated to be 993 feet long and the other is estimated to be 315 feet long.  In order for the system to function properly the voltage drop in these two wires should be the same.  In order to balance these two quantities a relationship between wire resistance and wire length is used to size the wires.  For the section of wire from the powerhouse to the ranch house we specified 6 gauge copper since a section of that length is already wired with this size wire.  The voltage drop for the wire run is less than 3%.  With the assumption of 6 gauge wire for the longer wire, the shorter wire should be 11 gauge.  Calculations are shown in Appendix D.

Since 11 gauge wire is not commonly available, we recommend using either ½ 12 gauge wire and ½ 10 gauge wire or adjusting the wire length to approximate the voltage drop from 11 gauge wire.

Each site will need a rectifier, a transformer, a diversion type charge controller and a diversion load.  The Outback MX-60 and the Xantrex C-60 can both be utilized as a diversion type charge controllers.

The diversion load takes excess power and diverts it to a heat load. This heat load can be utilized to heat water or a living space. If used with a water heater, a thermostat should be installed along with a secondary diversion load to protect the water heater from over heating and building up pressure. As a secondary heating load, water can be heated in an uncontained vessel such as a hot tub where no pressure is allowed to build up. For each site, a rectifier and transformer are required to convert the 120V wild AC to 12V DC.  One set is included with the micro-hydro system; the other will have to be purchased separately. The following schematics show the complete system, its components, and the associated wire sizes.  The recommended new components for phase II are summarized in Table 7, and shown in Figures 10 and 11.

Table 7: Summary of additional micro-hydro System components.

| Turbine and generator | Harris HV 600 |
| --- | --- |
| Pipe | 220 ft. schedule 40 3” PVC |
| 3 X elbows | 135° 3 inch PVC |
| 1 gate valve | 3 inch PVC |
| 2 Transformer and rectifier | 1 Included with HV 600 (120/12V) |
| 2 Diversion loads | 60A |
| 6 gauge copper wire | 793 feet (assumes 200 ft already laid) |
| 11 gauge copper wire | 315 feet |
| Intake system | Flume and sediment basin |
| Powerhouse | For turbine/generator |

Another important aspect of the micro-hydro system is the catchment system. Although we have not engineered this aspect of the system, it should be sturdy and able to withstand high winter flows and ice.  Due to the rocky nature of the geology, a large quantity of granite sand and gravel is expected to flow through the culvert and into the intake. The catchment should be sized to account for settling of this contaminant as it will grind up the bronze Pelton wheel.

The locations of the renewable energy system elements are shown in Figure 11.

Figure 9: Schematic of Phase II Ranch House

Figure 10: Schematic Phase II Long House

Figure 11: Location of system elements at Rock Creek Ranch site

# Economic Analysis

The overall cost for the proposed design was divided into two phases as per the plan of action. Costs for both sections were determined separately, as micro-hydro was assumed to be implemented later. Capital, operation and maintenance, replacement, and energy costs were studied to perform cost analysis over the life cycle of the project. The life cycle cost is given by:

Equation 1: Life Cycle cost

where,

| C | = | capital costs |
| --- | --- | --- |
| M | = | Operation and maintenance costs |
| R | = | costs for repair and replacement of equipments |
| E | = | costs for energy use, gasoline prices for generator |
| S | = | salvage value of the project |

The project is assumed to have a life cycle of 30 years with 4% discount rate. The salvage value is estimated to be 20% of the capital costs.

## Phase I

We evaluated two alternatives economically to present a cost effective design that meets the project objective. Alternative 1 involves 12 panels at 72 V at the ranch house with 2 maximum power point tracking controllers in parallel charging 10 batteries which are connected to a 2512 inverter. For the same alternative, the long house system entails 8 panels with 1 controller charging 6 batteries linked to a 1512 inverter. Alternative 2 examines fewer panels at both locations; for the ranch house 10 instead of 12 and for the long house 6 instead of 8. Except for the wire sizes, the rest of the system components for both alternatives are the same. A list of detailed system component and prices for both alternatives is summarized in Appendix E.

Capital cost is the expenditure required at the present time to implement the proposed design. Rock Creek Ranch already owns certain equipment such as panels, batteries, charge controller, and an inverter. Both options utilize existing elements of the system. The cost of these elements is not considered in the estimation of capital costs. Operation and maintenance costs are associated with the cost of labor required to operate and maintain the proposed PV system. The capital and present worth of O&M costs for both alternatives can be found in Tables 10 and 11.

Replacement and repair costs of system components are also accounted for in the life cycle cost analysis to allow for the wear and tear of the devices. The lifespan of the batteries was assumed to be 6 years as suggested by the client. We specified the lifespan of the charge controllers and inverters at 10 years. We estimated that the generator would need to be replaced every 15 years if micro-hydro were not put into operation. Present value calculations for replacement costs are summarized in Tables 10 and 11.

We also examined the non-renewable energy costs for the project.  These costs are mostly due to the use of a generator that is fueled by gasoline.  The Honda EM5000S gasoline generator at the site is reported in the manual to run at the rated power output of 4500W for 8.3 hours on 6.6 gallons of gas, a rate of 5.66kWh/gal.  At half-power, it reportedly runs for 12.8 hours.  Interpolating from these numbers, the reported charging rate of 14A is equivalent to 3.26kWh/gal.  Gasoline contains 34kWh/gallon.

The number of gallons required to meet loads at each location, assuming a 95% efficient battery charger, 80% efficient batteries, 95% efficient wire runs, and a 90% efficient inverter, are shown in Table 8.  For comparison purposes, numbers are shown for 100% dependency on the generator as well as after installation of the solar system.

Table 8: Gallons of gasoline required to meet loads at each location.

| Ranch house plus caretaker’s cabin |
| --- |
|  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual |
| No PV panels | 37.5 | 33.9 | 37.5 | 36.3 | 37.5 | 52.2 | 54.0 | 54.0 | 52.2 | 37.5 | 36.3 | 37.5 | 506.2 |
| 10 PV panels | 35.7 | 14.5 | 13.5 | 6.7 | 0.0 | 0.0 | 0.0 | 2.2 | 8.0 | 8.2 | 31.1 | 36.8 | 156.7 |
| 12 PV panels | 35.3 | 10.6 | 8.7 | 0.5 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 2.4 | 30.1 | 36.6 | 124.3 |
| Long house |
| No PV panels | 11.0 | 10.0 | 11.0 | 10.7 | 11.0 | 20.1 | 20.8 | 20.8 | 20.8 | 11.0 | 10.7 | 11.0 | 169.1 |
| 6 PV panels | 8.9 | 2.9 | 1.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.7 | 3.1 | 0.0 | 7.5 | 9.6 | 33.6 |
| 8 PV panels | 8.1 | 0.7 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 6.6 | 9.1 | 24.5 |

Based on the estimated generator use, we determined gasoline costs for a 30 year period (Table 9).  The price of gas at the present time was assumed to be $2.93/gal.  Fuel was assumed to increase at a rate of 1.7 % over the general inflation rate (CNN, 2006).  A discount rate of 4% was used.  Alternative 1 is 12 panels at the ranch house and 8 panels at the long house; alternative 2 is 10 panels at the ranch house and 6 panels at the long house.

Table 9: Energy costs for alternatives

| Case | Estimated Energy Cost |
| --- | --- |
| No Panels | $42,761 |
| Alternative 1 | $9,419 |
| Alternative 2 | $12,049 |

The life cycle cost analysis for both alternatives is summarized in Table 10 and Table 11. The cost for excavating trenches for wire runs is a very rough estimate.  The prices of other components of a PV system such as circuit breakers and miscellaneous items are also estimated.

Table 10: Alternative 1 life cycle costs

| Ranch House |
| --- |
| Capital | Single Present Worth Year | Capital costs | Present Worth Factor | Present Worth |
| Item |  | $ | # | $ |
| PV Panels (2) |  | 1,236.00 | 1.00 | 1,236.00 |
| Charge Controller (1) |  | 649.00 | 1.00 | 649.00 |
| Wires |  | 1298.80 | 1.00 | 1298.80 |
| Fuse Slow Blow |  | 15.21 | 1.00 | 15.21 |
| Batteries (10) |  | 1,999.50 | 1.00 | 1,999.50 |
| Mounts |  | 840.00 | 1.00 | 840.00 |
| Installation |  | 500.00 | 1.00 | 500.00 |
| 175 Amp disconnect |  | 375.00 | 1.00 | 375.00 |
| Trench to orchard |  | 500.00 | 1.00 | 500.00 |
| AC/DC panels, misc |  | 500.00 | 1.00 | 500.00 |
| Total |  | 7913.51 |  | 7913.51 |
| O&M Annual |  | Costs ($/year) | Present Worth Factor | Present Worth |
|  |  | 100 | 17.29 | 1729.20 |
| Energy |  | Costs ($/year) | Present Worth Factor | Present Worth |
| Fuel costs |  | 364.08 | 21.61 | 7868.38 |
| Replacement/Repair |  | Costs ($/year) | Present Worth Factor | Present Worth |
| Battery | 6 | 1,999.50 | 0.79 | 1,580.23 |
| Battery | 12 | 1,999.50 | 0.62 | 1,248.88 |
| Battery | 18 | 1,999.50 | 0.49 | 987.01 |
| Battery | 24 | 1,999.50 | 0.39 | 780.05 |
| Charge Controller | 10 | 649.00 | 0.68 | 438.44 |
| Charge Controller | 20 | 649.00 | 0.46 | 296.20 |
| Inverter | 15 | 1,299.00 | 0.56 | 721.29 |
| Generator | 15 | 2,681.95 | 0.56 | 1,489.19 |
| Total |  |  |  | 7,541.29 |
| Salvage Value |  | 2,578.46 | 0.31 | 794.99 |
| LCC |  |  |  | 24,257.39 |
| Long House |
| Capital | Single Present Worth Year | Capital costs | Present Worth Factor | Present Worth |
| Item |  | $ | # | $ |
| Panels |  | 958.32 | 1.00 | 958.32 |
| Inverter |  | 799.00 | 1.00 | 799.00 |
| Charge Controller |  | 167.16 | 1.00 | 167.16 |
| Fuse Slow Blow |  | 15.21 | 1.00 | 15.21 |
| Wires |  | 69.56 | 1.00 | 69.56 |
| Roof Mount |  | 258.00 | 1.00 | 258.00 |
| 100 Amp disconnect |  | 325.00 | 1.00 | 325.00 |
| AC Panel, misc |  | 350.00 | 1.00 | 350.00 |
| Installation |  | 500.00 | 1.00 | 500.00 |
| Total |  | 3442.25 |  | 3442.25 |
| O&M Annual |  | Costs ($/year) | Present Worth Factor | Present Worth |
|  |  | 100 | 17.29 | 1729.20 |
| Energy |  | Costs ($/year) | Present Worth Factor | Present Worth |
| Fuel costs |  | 71.77 | 21.61 | 1551.02 |
| Replacement/Repair |  | Costs ($/year) | Present Worth Factor | Present Worth |
| Battery | 6 | 1,199.70 | 0.79 | 948.14 |
| Battery | 12 | 1,199.70 | 0.62 | 749.33 |
| Battery | 18 | 1,199.70 | 0.49 | 592.21 |
| Battery | 24 | 1,199.70 | 0.39 | 468.03 |
| Charge Controller | 10 | 167.16 | 0.68 | 113.67 |
| Charge Controller | 20 | 167.16 | 0.46 | 76.89 |
| Inverter | 15 | 799.00 | 0.56 | 443.66 |
| Total |  |  |  | 3,391.93 |
| Salvage Value |  | 545.42 | 0.31 | 168.16 |
| LCC |  |  |  | 9,946.25 |

Table 11: Alternative 2 life cycle costs

| Ranch House |
| --- |
| Capital | Single Present Worth Year | Capital costs | Present Worth Factor | Present Worth |
| Item |  | $ | # | $ |
| Charge Controller |  | 649.00 | 1.00 | 649.00 |
| Wires |  | 1,694.36 | 1.00 | 1,694.36 |
| Batteries |  | 1,999.50 | 1.00 | 1,999.50 |
| Fuse Slow Blow |  | 15.21 | 1.00 | 15.21 |
| Mounts |  | 840.00 | 1.00 | 840.00 |
| 175 Amp disconnect |  | 375.00 | 1.00 | 375.00 |
| Trench to orchard |  | 500.00 | 1.00 | 500.00 |
| AC/DC panels, misc |  | 500.00 | 1.00 | 500.00 |
| Installation |  | 500.00 | 1.00 | 500.00 |
| Total |  | 7073.07 |  | 7073.07 |
| O&M Annual |  | Costs ($/year) | Present Worth Factor | Present Worth |
|  |  | 100.00 | 17.29 | 1,729.20 |
| Energy |  | Costs ($/year) | Present Worth Factor | Present Worth |
| Fuel costs |  | 459.09 | 21.61 | 9,921.72 |
| Replacement/Repair |  | Costs ($/year) | Present Worth Factor | Present Worth |
| Battery | 6 | 1,999.50 | 0.79 | 1,580.23 |
| Battery | 12 | 1,999.50 | 0.62 | 1,248.88 |
| Battery | 18 | 1,999.50 | 0.49 | 987.01 |
| Battery | 24 | 1,999.50 | 0.39 | 780.05 |
| Charge Controller | 10 | 649.00 | 0.68 | 438.44 |
| Charge Controller | 20 | 649.00 | 0.46 | 296.20 |
| Inverter | 15 | 1,299.00 | 0.56 | 721.29 |
| Generator | 15 | 2,681.95 | 0.56 | 1,489.19 |
| Total |  |  |  | 7,541.29 |
| Salvage Value |  | 2,627.21 | 0.31 | 810.02 |
| LCC |  |  |  | 25,455.26 |
| Long House |
| Capital | Single Present Worth Year | Capital costs | Present Worth Factor | Present Worth |
| Item |  | $ | # | $ |
| Inverter |  | 799.00 | 1.00 | 799.00 |
| Charge Controller |  | 167.16 | 1.00 | 167.16 |
| Fuse Slow Blow |  | 15.21 | 1.00 | 15.21 |
| Wires |  | 69.56 | 1.00 | 69.56 |
| Roof Mount |  | 258.00 | 1.00 | 258.00 |
| 100 Amp disconnect |  | 325.00 | 1.00 | 325.00 |
| AC Panel, misc |  | 350.00 | 1.00 | 350.00 |
| Installation |  | 500.00 | 1.00 | 500.00 |
| Total |  | 2483.93 |  | 2483.93 |
| O&M Annual |  | Costs ($/year) | Present Worth Factor | Present Worth |
|  |  | 100 | 17.29 | 1729.20 |
| Energy |  | Costs ($/year) | Present Worth Factor | Present Worth |
| Fuel costs |  | 98.42 | 21.61 | 2127.00 |
| Replacement/Repair |  | Costs ($/year) | Present Worth Factor | Present Worth |
| Battery | 6 | 1,199.70 | 0.79 | 948.14 |
| Battery | 12 | 1,199.70 | 0.62 | 749.33 |
| Battery | 18 | 1,199.70 | 0.49 | 592.21 |
| Battery | 24 | 1,199.70 | 0.39 | 468.03 |
| Charge Controller | 10 | 167.16 | 0.68 | 113.67 |
| Charge Controller | 20 | 167.16 | 0.46 | 76.89 |
| Inverter | 15 | 799.00 | 0.56 | 443.66 |
| Total |  |  |  | 3,391.93 |
| Salvage Value |  | 353.76 | 0.31 | 109.07 |
| LCC |  |  |  | 9,623.00 |

The life cycle cost of option 1 is $34,203 and of option 2 is $35,078.  Option 1 includes a total of 20 panels whereas option 2 proposes 16 panels. The difference between the costs of two options is due to energy costs. With 20 panels, a larger investment at the present time saves the expenditure on gasoline over the 30 year lifespan.

We also performed a sensitivity analysis on the costs of two alternatives assuming changes in the escalation rate (the assumed increase in gas prices above inflation) (Table 12). As the assumed fuel costs increase, a larger difference is observed between the two options. A discontinuity exists when escalation rate is equal to the discount rate as the mathematical expression crashes.

Table 12: Sensitvity on life cycle costs based on escalation rate

| Esc. Rate | PW Factor | 16 panel option | 20 panel option |
| --- | --- | --- | --- |
| 2.00% | 22.52 | $35,513.56 | $34,093.47 |
| 2.50% | 24.14 | $36,418.49 | $34,800.92 |
| 3.00% | 25.92 | $37,409.19 | $35,575.43 |
| 3.50% | 27.86 | $38,494.71 | $36,424.06 |
| 4.00% | N/A | N/A | N/A |
| 4.50% | 32.34 | $40,991.34 | $38,375.86 |
| 5.00% | 34.92 | $42,425.91 | $39,497.38 |
| 5.50% | 37.74 | $44,002.46 | $40,729.89 |
| 6.00% | 40.85 | $45,736.17 | $42,085.26 |
| 6.50% | 44.28 | $47,643.87 | $43,576.66 |
| 7.00% | 48.04 | $49,744.28 | $45,218.70 |
| 7.50% | 52.19 | $52,058.11 | $47,027.60 |

## Phase II

The second phase of the design is to harness energy from a culvert located 315 ft. south of longhouse.  We evaluated the present worth for implementation of this phase. The breakdown of prices for each component of the micro-hydro system can be found in Appendix E. An important component of a micro-hydro system is a settling basin that collects all the debris to minimize damage to the turbine. We have not designed a settling basin for this project due to time and expertise constraints.  All construction costs are very rough estimates.  The diversion load shown in the table can be purchased if no other suitable diversion load already exists.  The life cycle cost analysis of phase II is shown in Table 13. With the completion of phase II, we expect that the energy costs of phase I will be replaced by the cost of micro-hydro system. Application of micro-hydro is more cost effective than using a generator for winter months.

Table 13: Life cycle cost for Phase II (micro-hydro)

| Capital | Single Present Worth Year | Capital costs | Present Worth Factor | Present Worth |
| --- | --- | --- | --- | --- |
| Item |  | $ | # | $ |
| 600 W Pelton Wheel with Rectifier (e) |  | 2,500.00 | 1.00 | 2,500.00 |
| 2nd Transformer/Rectifier (e) |  | 50.00 | 1.00 | 50.00 |
| Diversion Load (e) |  | 450.00 | 1.00 | 450.00 |
| Pipe |  | 538.75 | 1.00 | 538.75 |
| Wires to RH |  | 1538.42 | 1.00 | 1538.42 |
| Wires to LH |  | 239.40 | 1.00 | 239.40 |
| Intake/sediment basin |  | 2000.00 | 1.00 | 2000.00 |
| Trench |  | 500.00 | 1.00 | 500.00 |
| Powerhouse |  | 500.00 | 1.00 | 500.00 |
| Construction costs |  | 2000.00 | 1.00 | 2000.00 |
| Total |  | 10,316.57 |  | 10,316.57 |
| O&M Annual |  | Costs ($/year) | Present Worth Factor | Present Worth |
|  |  | 100.00 | 17.29 | 1,729.20 |
| Replacement/Repair |  | Costs ($/year) | Present Worth Factor | Present Worth |
| Pelton Wheel | 15 | 2,500.00 | 0.56 | 1,388.16 |
| Transformer/Rectifier | 15 | 50.00 | 0.56 | 27.76 |
| Subtotal |  |  |  | 3145.12 |
| Salvage Value |  | 107.75 | 1.00 | 107.75 |
| LCC |  |  |  | 13,326.18 |

# Recommendations

Based on the design and cost analysis, Survey and Design Experts propose the following:

- A PV system of 12 115W panels at the ranch house with two MX 60 MPPT charge controllers in parallel connected to 10 6V UL-16 batteries and a 2512 inverter; a system of 8 75W panels at the long house with one Xantrex C-60 charge controller linked to 6 6V UL-16 batteries and a 1512 inverter OR

- A PV system consisting of 10 115W panels at the ranch house and 6 75W panels at the long house;

- A micro-hydro system with a 600W AC turbine/generator with shunt controllers, transformer-rectifiers, and diversion loads.

# References

Gas prices October 20, 2006:

http://www.automotive.com/gas-prices/33/california/humboldt/hoopa/index.html

Gas annual growth rate:

http://money.cnn.com/2006/05/18/news/economy/pluggedin_fortune/index.htm

GRS, 2006. Gasquet Ranger Station http://www.wrcc.dri.edu/cgi-bin/cliMAIN.pl?ca3357

HP, 2006. Data: Hydro Induction Brushless Turbines http://www.hipowerhydro.com/Data.htm

OSE, 2006. Sizing Irrigation Mainlines and Fittings

http://extension.oregonstate.edu/catalog/pdf/pnw/pnw290.pdf

Smith River Alliance, Rock Creek Ranch. http://www.smithriveralliance.org/rcranch.html

WSU, 2003. http://www.energy.wsu.edu/documents/building/res/ht_pmp_water_htrs.pdf

# Appendices

## Available Data

### Solar Insolation

| Location Gasquet California | Elevation | 500 ft. |
| --- | --- | --- |
| Latitude 41° 50' 45" | 41.8 | Agency | USFS |
| Longitude 123° 58' 45" | 124 | NESS ID | 3239C028 |
|  |  | NWS ID | 040102 |

| Months | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Insolation (kWh/day) | 0.76 | 1.86 | 2.84 | 4.04 | 5.6 | 6.9 | 7.19 | 6 | 4.74 | 2.6 | 1.12 | 0.54 |
| Tilt = 42°: | 0.703 | 2.421 | 3.176 | 3.934 | 4.901 | 5.689 | 6.077 | 5.677 | 5.358 | 3.449 | 1.091 | 0.491 |
| Monthly tilt = φ - δ: | 0.65 | 2.48 | 3.24 | 4.16 | 5.52 | 6.69 | 7.02 | 6.13 | 5.5 | 3.54 | 1.03 | 0.44 |
| Static tilt = φ: | 0.722 | 2.469 | 3.249 | 4.037 | 5.045 | 5.866 | 6.262 | 5.831 | 5.479 | 3.516 | 1.120 | 0.505 |
| Static tilt = φ - 15° | 0.755 | 2.347 | 3.233 | 4.204 | 5.448 | 6.472 | 6.859 | 6.152 | 5.465 | 3.335 | 1.152 | 0.531 |
| Insolation available after shading at orchard, assuming tree cuts: | 29% | 90% | 77% | 77% | 77% | 93% | 94% | 88% | 87% | 86% | 54% | 17% |

### Micro-hydro

| Station | Where the tripod is set. |
| --- | --- |
| BS | Back shoot |
| FS | Forward Shoot |
| HI | Height of the instrument |
| Elevation |  |
| Station | BS (ft) | HI (ft) | FS (ft) | Elevation (ft) |
|  | + |  | - |  |
| Temporary bench mark | 5.67 | 105.67 |  | 100 |
| Station 1 |  |  | 0.96 | 104.71 |
|  | 11.72 | 116.43 |  |  |
| Station 2 |  |  | 4.61 | 111.82 |
|  | 14.86 | 126.68 |  |  |
| Station 3 |  |  | 2.32 | 124.36 |
|  | 25.04 | 149.4 |  |  |
| Station 4 |  |  | 1.86 | 147.54 |
|  | 22.23 | 169.77 |  |  |
| Station 5 |  |  | 1.18 | 168.59 |
| Station 6 |  |  |  | 3.32 |
| Total elevation (ft) |  |  |  | 171.91 |
| Net elevation (ft) |  |  |  | 71.91 |

## Load Analysis

Ranch House summer: June - September

|  |  |  |  |  |  |  |  |  | Whr /day | Whr /day |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Watts | Watts | Use | Use | Day |  |  |
| Location | Appliance | Notes | # | V | A | AC | DC | Hrs/Day | Days/Wk | in Wk | AC | DC |
| South Living Room |  |  |  |  |  |  |  |  |  |  |  |  |
|  | radio | phantom | 1 |  |  | 11 |  |  |  | 7 | 0 |  |
|  | radio | in use | 1 |  |  | 24 |  | 8 | 1 | 7 | 27 |  |
|  | CFL bulb | east side | 1 |  |  | 27 |  | 2 | 7 | 7 | 54 |  |
|  |  | west side | 1 |  |  | 26 |  | 2 | 7 | 7 | 52 |  |
|  | light bulb | Floor lamp | 1 |  |  | 17 |  |  |  | 7 | 0 |  |
|  | vacuum | in use | 1 |  |  | 1150 |  | 0.5 | 2 | 7 | 164 |  |
| Kitchen |  |  |  |  |  |  |  |  |  |  |  |  |
|  | light fixture | brown (2 bulbs) | 2 |  |  | 13 |  | 2 | 7 | 7 | 52 |  |
|  |  | above sink (2) | 1 |  |  | 39 |  | 2 | 7 | 7 | 78 |  |
|  |  | above stove (2) | 2 |  |  | 15 |  | 2 | 7 | 7 | 60 |  |
|  | coffee grinder | shade grown | 1 |  |  | 107 |  | 0.03 | 7 | 7 | 4 |  |
|  | exhaust fan | in use | 1 |  |  | 75.6 |  | 2 | 1 | 7 | 22 |  |
|  | cell phone | stand-by | 1 | 12 | 0.5 |  | 6 | 23.9 | 7 | 7 |  | 143 |
|  |  | in use | 1 | 12 | 2.1 |  | 25 | 1 | 1 | 7 |  | 3.6 |
|  | blender |  | 1 |  |  | 255 |  | 0.5 | 1 | 7 | 18 |  |
|  | fridge | Sunfrost RF-19 |  |  |  |  |  |  |  |  |  | 770 |
| Laundry |  |  |  |  |  |  |  |  |  |  |  |  |
|  | dryer | Maytag performa | 1 |  |  | 300 |  | 1.4 | 3 | 7 | 180 |  |
|  | washer | Roper | 1 |  |  | 725 |  | 1 | 3 | 7 | 311 |  |
|  | fridge | Sunfrost R-10 | 1 |  |  |  |  |  |  | 7 |  | 280 |
|  | light fixture | south | 1 |  |  | 13 |  | 2 | 7 | 7 | 26 |  |
|  |  | north | 1 |  |  | 20 |  | 2 | 7 | 7 | 40 |  |
|  |  | hallway | 1 |  |  | 15 |  | 2 | 7 | 7 | 30 |  |
|  |  | south solar tube | 1 |  |  | 23 |  | 2 | 7 | 7 | 46 |  |
|  |  | north solar tube | 1 |  |  | 23 |  | 2 | 7 | 7 | 46 |  |
| Bedroom Hallway |  |  |  |  |  |  |  |  |  | 7 |  |  |
|  | light fixture |  | 1 |  |  | 15 |  | 2 | 7 | 7 | 30 |  |
| Tool Room |  |  |  |  |  |  |  |  |  | 7 | 0 |  |
|  | battery charger | Makita | 1 |  |  | 35 |  | 0.5 | 4 | 7 | 10 |  |
|  |  | Makita | 1 |  |  | 35 |  | 0.5 | 4 | 7 | 10 |  |
|  |  | Makita | 1 |  |  | 60 |  | 0.5 | 4 | 7 | 17 |  |
|  | light fixture | above sink | 1 |  |  | 15 |  | 2 | 7 | 7 | 30 |  |
| North Bedroom |  |  |  |  |  |  |  |  |  | 7 |  |  |
|  | light fixture | 2 bulbs | 1 |  |  | 35 |  | 2 | 7 | 7 | 70 |  |
| N.East Bedroom |  |  |  |  |  |  |  |  |  | 7 |  |  |
|  | light fixture | ceiling | 1 |  |  | 16 |  | 2 | 7 | 7 | 32 |  |
|  |  | Floor lamp | 1 |  |  | 20 |  | 2 | 7 | 7 | 40 |  |
| N.West Bedroom (with paintings) |  |  |  |  |  |  |  |  | 7 | 0 |  |
|  | light fixture | floor lamp | 1 |  |  | 14 |  | 2 | 7 | 7 | 28 |  |
|  |  | ceiling | 1 |  |  | 20 |  | 2 | 7 | 7 | 40 |  |
|  |  | closet (overhead) | 1 |  |  | unused |  |  |  | 7 |  |  |
|  | fan |  | 1 |  |  | 36 |  |  |  | 7 | 0 |  |
| South Bedroom |  |  |  |  |  |  |  |  |  | 7 |  |  |
|  | light fixture | floor lamp | 1 |  |  | 15 |  | 2 | 7 | 7 | 30 |  |
|  |  | ceiling | 1 |  |  | 15 |  | 2 | 7 | 7 | 30 |  |
|  | space heater |  | 1 |  |  | 600-1500 |  |  |  | 7 |  |  |
| South Bathroom (off of bedroom) |  | 1 |  |  |  |  |  |  | 7 |  |  |
|  | light fixture | 2 bulbs | 2 |  |  | 14 |  | 2 | 7 | 7 | 56 |  |
|  |  | 2 bulbs | 2 |  |  | 14 |  | 2 | 7 | 7 | 56 |  |
|  |  | overhead fan | 1 |  |  | 133.2 |  | 0 | 7 | 7 | 0 |  |
|  | fan | exhaust | 1 |  |  | 15 |  | 0.5 | 7 | 7 | 8 |  |
| East Living Room |  |  |  |  |  |  |  |  |  | 7 |  |  |
|  | light fixture |  | 1 |  |  | 20 |  | 2 | 7 | 7 | 40 |  |
|  |  | 2 bulbs | 2 |  |  | 20 |  | 2 | 7 | 7 | 80 |  |
| Outside Deck |  |  |  |  |  |  |  |  |  | 7 | 0 |  |
|  | light fixture | s.deck | 1 |  |  | 120 |  | 2 | 1 | 7 | 34 |  |
|  |  | east side | 1 |  |  | 20 |  | 2 | 1 | 7 | 6 |  |
|  |  | N. east | 1 |  |  | 120 |  | 2 | 1 | 7 | 34 |  |
|  |  | W. path | 1 |  |  | 120 |  | 2 | 1 | 7 | 34 |  |
|  |  | W. porch | 1 |  |  | 15 |  | 2 | 1 | 7 | 4 |  |
| Garage |  |  |  |  |  |  |  |  |  | 7 |  |  |
|  | lights | (don't use) | 2 |  |  | 100 |  |  |  | 7 |  |  |
|  | air compressor |  | 1 |  |  | 1800 |  |  |  | 7 | 0 |  |
|  | shop vacuum |  | 1 |  |  | 1440 |  |  |  | 7 | 0 |  |
|  | lights | in workshop | 2 |  |  | 23 |  | 8 | 1 | 7 | 53 |  |
|  | radio | workshop | 1 |  |  | 1 |  |  |  | 7 | 0 |  |
|  | light | workshop | 1 |  |  | 13 |  |  |  | 7 | 0 |  |
|  | light bulb | outside | 1 |  |  | 100 |  |  |  | 7 | 0 |  |
|  |  | outside | 1 |  |  | 75 |  |  |  | 7 | 0 |  |
|  | battery charger | 4 hrs. | 1 |  |  | 2400 |  |  |  | 7 |  |  |
|  |  | 2 hrs. | 1 |  |  | 480 |  |  |  | 7 |  |  |
| Generator Shed |  |  |  |  |  |  |  |  |  | 7 |  |  |
|  | lights | 3 bulbs | 3 |  |  | 25 |  | 1 | 1 | 7 | 11 |  |
|  | generator | Honda | 1 |  |  | 13-14 amps |  |  |  |  |  |  |
|  |  | Onen | 1 |  |  | 20 amps |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | AC Whr/day | DC Whr/day |
|  |  |  |  |  |  |  |  |  |  |  | Total | Total |
|  |  |  |  |  |  |  |  |  |  |  | 1993 | 1197 |

Ranch House winter: October - May

|  |  |  |  |  |  |  |  |  | Whr /day | Whr /day |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Watts | Watts | Use | Use | Days |  |  |
| Location | Appliance | Notes | # | V | A | AC | DC | Hrs/Day | Days/Wk | in Wk | AC | DC |
| South Living Room |  |  |  |  |  |  |  |  |  |  |  |  |
|  | radio | phantom | 1 |  |  | 11 |  |  |  | 7 | 0 |  |
|  | radio | in use | 1 |  |  | 24 |  | 8 | 7 | 7 | 192 |  |
|  | CFL bulb | east side | 1 |  |  | 27 |  | 1 | 7 | 7 | 27 |  |
|  |  | west side | 1 |  |  | 26 |  | 1 | 7 | 7 | 26 |  |
|  | light bulb | Floor lamp | 1 |  |  | 17 |  | 8 | 7 | 7 | 136 |  |
|  | vacuum | in use | 1 |  |  | 1150 |  | 0.5 | 1 | 7 | 82 |  |
| Kitchen |  |  |  |  |  |  |  |  |  |  |  |  |
|  | light fixture | brown (2 bulbs) | 2 |  |  | 13 |  | 1 | 7 | 7 | 26 |  |
|  |  | above sink (2) | 1 |  |  | 39 |  | 1 | 7 | 7 | 39 |  |
|  |  | above stove (2) | 2 |  |  | 15 |  | 1 | 7 | 7 | 30 |  |
|  | coffee grinder |  | 1 |  |  | 107 |  | 0.02 | 7 | 7 | 2 |  |
|  | exhaust fan | in use | 1 |  |  | 75.6 |  | 0.5 | 1 | 7 | 5 |  |
|  | cell phone | stand-by | 1 | 12 | 0.5 |  | 6 | 23.6 | 7 | 7 |  | 142 |
|  |  | in use | 1 | 12 | 2.1 |  | 25 | 3 | 1 | 7 |  | 10.8 |
|  | blender |  | 1 |  |  | 255 |  | 0 | 1 | 7 | 0 |  |
|  | fridge | Sunfrost RF-19 |  |  |  |  |  |  |  |  |  | 400 |
| Laundry |  |  |  |  |  |  |  |  |  |  |  |  |
|  | dryer | Maytag performa | 1 |  |  | 300 |  | 1.4 | 2 | 7 | 120 |  |
|  | washer | Roper | 1 |  |  | 725 |  | 1 | 2 | 7 | 207 |  |
|  | fridge | Sunfrost R-10 | 1 |  |  |  |  |  |  | 7 |  | 0 |
|  | light fixture | south | 1 |  |  | 13 |  | 1 | 7 | 7 | 13 |  |
|  |  | north | 1 |  |  | 20 |  | 1 | 7 | 7 | 20 |  |
|  |  | hallway | 1 |  |  | 15 |  | 1 | 7 | 7 | 15 |  |
|  |  | south solar tube | 1 |  |  | 23 |  | 1 | 7 | 7 | 23 |  |
|  |  | north solar tube | 1 |  |  | 23 |  | 1 | 7 | 7 | 23 |  |
| Bedroom Hallway |  |  |  |  |  |  |  |  |  | 7 |  |  |
|  | light fixture |  | 1 |  |  | 15 |  | 1 | 7 | 7 | 15 |  |
| Tool Room |  |  |  |  |  |  |  |  |  | 7 | 0 |  |
|  | battery charger | Makita | 1 |  |  | 35 |  | 0.5 | 2 | 7 | 5 |  |
|  |  | Makita | 1 |  |  | 35 |  | 0.5 | 2 | 7 | 5 |  |
|  |  | Makita | 1 |  |  | 60 |  | 0.5 | 2 | 7 | 9 |  |
|  | light fixture | above sink | 1 |  |  | 15 |  | 1 | 7 | 7 | 15 |  |
| North Bedroom |  |  |  |  |  |  |  |  |  | 7 |  |  |
|  | light fixture | 2 bulbs | 1 |  |  | 35 |  | 1 | 7 | 7 | 35 |  |
| N.East Bedroom |  |  |  |  |  |  |  |  |  | 7 |  |  |
|  | light fixture | ceiling | 1 |  |  | 16 |  | 1 | 7 | 7 | 16 |  |
|  |  | Floor lamp | 1 |  |  | 20 |  | 1 | 7 | 7 | 20 |  |
| N.West Bedroom (with paintings) |  |  |  |  |  |  |  |  | 7 | 0 |  |
|  | light fixture | floor lamp | 1 |  |  | 14 |  | 1 | 7 | 7 | 14 |  |
|  |  | ceiling | 1 |  |  | 20 |  | 1 | 7 | 7 | 20 |  |
|  |  | closet (overhead) | 1 |  |  | unused |  |  |  | 7 |  |  |
|  | fan |  | 1 |  |  | 36 |  |  |  | 7 | 0 |  |
| South Bedroom |  |  |  |  |  |  |  |  |  | 7 |  |  |
|  | light fixture | floor lamp | 1 |  |  | 15 |  | 1 | 7 | 7 | 15 |  |
|  |  | ceiling | 1 |  |  | 15 |  | 1 | 7 | 7 | 15 |  |
|  | space heater |  | 1 |  |  | 600-1500 |  |  |  | 7 |  |  |
| South Bathroom (off of bedroom) |  | 1 |  |  |  |  |  |  | 7 |  |  |
|  | light fixture | 2 bulbs | 2 |  |  | 14 |  | 1 | 7 | 7 | 28 |  |
|  |  | 2 bulbs | 2 |  |  | 14 |  | 1 | 7 | 7 | 28 |  |
|  |  | overhead fan | 1 |  |  | 133.2 |  | 0 | 7 | 7 | 0 |  |
|  | fan | exhaust | 1 |  |  | 15 |  | 0 | 7 | 7 | 0 |  |
| East Living Room |  |  |  |  |  |  |  |  |  | 7 |  |  |
|  | light fixture |  | 1 |  |  | 20 |  | 1 | 7 | 7 | 20 |  |
|  |  | 2 bulbs | 2 |  |  | 20 |  | 1 | 7 | 7 | 40 |  |
| Outside Deck |  |  |  |  |  |  |  |  |  | 7 | 0 |  |
|  | light fixture | s.deck | 1 |  |  | 120 |  | 0 | 1 | 7 | 0 |  |
|  |  | east side | 1 |  |  | 20 |  | 0 | 1 | 7 | 0 |  |
|  |  | N. east | 1 |  |  | 120 |  | 0 | 1 | 7 | 0 |  |
|  |  | W. path | 1 |  |  | 120 |  | 0 | 1 | 7 | 0 |  |
|  |  | W. porch | 1 |  |  | 15 |  | 0 | 1 | 7 | 0 |  |
| Garage |  |  |  |  |  |  |  |  |  | 7 |  |  |
|  | lights | (don't use) | 2 |  |  | 100 |  |  |  | 7 |  |  |
|  | air compressor |  | 1 |  |  | 1800 |  |  |  | 7 | 0 |  |
|  | shop vacuum |  | 1 |  |  | 1440 |  |  |  | 7 | 0 |  |
|  | lights | in workshop | 2 |  |  | 23 |  | 16 | 1 | 7 | 105 |  |
|  | radio | workshop | 1 |  |  | 1 |  |  |  | 7 | 0 |  |
|  | light | workshop | 1 |  |  | 13 |  |  |  | 7 | 0 |  |
|  | light bulb | outside | 1 |  |  | 100 |  |  |  | 7 | 0 |  |
|  |  | outside | 1 |  |  | 75 |  |  |  | 7 | 0 |  |
|  | battery charger | 4 hrs. | 1 |  |  | 2400 |  |  |  | 7 |  |  |
|  |  | 2 hrs. | 1 |  |  | 480 |  |  |  | 7 |  |  |
| Generator Shed |  |  |  |  |  |  |  |  |  | 7 |  |  |
|  | lights | 3 bulbs | 3 |  |  | 25 |  | 1 | 1 | 7 | 11 |  |
|  | generator | Honda | 1 |  |  | 13-14 amps |  |  |  |  |  |  |
|  |  | Onen | 1 |  |  | 20 amps |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | AC Whr/day | DC Whr/day |
|  |  |  |  |  |  |  |  |  |  |  | Total | Total |
|  |  |  |  |  |  |  |  |  |  |  | 1402 | 552 |

Long House Summer: June-Sept

|  |  |  |  | Watts | Watts | Use | Use | Days | Whr | Whr |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Appliance | # | Volts | Amps | AC | DC | Hrs/Day | Days/Wk | in Week | AC | DC |
| General Lights | 4 |  |  | 26 |  | 3 | 7 | 7 | 312 |  |
| General Lights | 4 |  |  | 26 |  | 3 | 7 | 7 | 312 |  |
| Sunfrost R10 Fridge | 1 |  |  |  |  |  |  |  | 280 |  |
| Coffee Grinder | 1 |  |  | 107 |  | 0.02 | 7 | 7 | 1.8 |  |
| Blender | 1 |  |  | 225 |  | 0.02 | 7 | 7 | 3.8 |  |
| Bathroom Fan | 1 |  |  | 15 |  | 1 | 7 | 7 | 15 |  |
| Composting Toilet Fan | 1 |  |  | 12 |  | 5 | 7 | 7 | 60 |  |
| Bathroom Lights | 2 |  |  | 26 |  | 1 | 7 | 7 | 52 |  |
| battery charger | 1 |  |  | 35 |  | 2 | 1 | 7 | 10 |  |
| water pump | 1 |  |  | 72 |  | 3 | 7 | 7 | 216 |  |
|  |  |  |  |  |  |  |  |  | AC | DC |
|  |  |  |  |  |  |  |  |  | Whr/day | Whr/day |
|  |  |  |  |  |  |  |  |  | 1263 | 0 |
| Composting Toilet (existing) |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Watts | Watts | Use | Use | Days | Whr | Whr |
| Appliance | # | Volts | Amps | AC | DC | Hrs/Day | Days/Wk | AC | DC |
| Fan | 1 | 12 | 1 |  | 12 | 10 | 7 | 7 |  | 120 |
| Light (CFL) | 1 |  |  |  | 13 | 3 | 7 | 7 |  | 39 |
|  |  |  |  |  |  |  |  |  | AC | DC |
|  |  |  |  |  |  |  |  |  | Whr/day | Whr/day |
|  |  |  |  |  |  |  |  |  | -- | 159 |
| Long House (April, May & October + winter months) |
|  |  |  |  | Watts | Watts | Use | Use | Days | Whr | Whr |
| Appliance | # | Volts | Amps | AC | DC | Hrs/Day | Days/Wk | in Week | AC | DC |
| General Lights | 4 |  |  | 26 |  | 4 | 2 | 7 | 119 |  |
| General Lights | 4 |  |  | 26 |  | 4 | 2 | 7 | 119 |  |
| Sunfrost R10 Fridge | 1 |  |  |  |  |  |  |  | 170 |  |
| Coffee Grinder | 1 |  |  | 107 |  | 0.02 | 2 | 7 | 0.5 |  |
| Blender | 1 |  |  | 225 |  | 0.02 | 2 | 7 | 1.1 |  |
| Bathroom Fan | 1 |  |  | 15 |  | 1 | 2 | 7 | 4 |  |
| Composting Toilet Fan | 1 |  |  | 12 |  | 5 | 7 | 7 | 60 |  |
| Bathroom Lights | 2 |  |  | 26 |  | 1 | 2 | 7 | 15 |  |
| battery charger | 1 |  |  | 35 |  | 2 | 5 | 7 | 50 |  |
| water pump | 1 |  |  | 72 |  | 3 | 7 | 7 | 216 |  |
|  |  |  |  |  |  |  |  |  | AC | DC |
|  |  |  |  |  |  |  |  |  | Whr/day | Whr/day |
|  |  |  |  |  |  |  |  |  | 754 | 0 |

Caretaker Cabin Loads

| Summer |
| --- |
|  |  | Watts | Watts | Use | Use | Days | Whr |
| Appliance | # | AC | DC | Hrs/Day | Days/Wk | in Week | AC |
| Lights | 3 | 26 |  | 4 | 7 | 7 | 312 |
| Fridge (Sunfrost R10) | 1 |  |  |  |  |  | 170 |
| radio | 1 | 15 |  | 1 | 7 | 7 | 15 |
| coffee grinder | 1 | 107 |  | 0.02 | 7 | 7 | 1.8 |
|  |  |  |  |  |  |  | AC |
|  |  |  |  |  |  |  | Whr/Day |
|  |  |  |  |  |  |  | 499 |
| Winter |
|  |  | Watts | Watts | Use | Use | Days | Whr |
| Appliance | # | AC | DC | Hrs/Day | Days/Wk | in Week | AC |
| Lights | 3 | 26 |  | 5 | 7 | 7 | 390 |
| Fridge (Sunfrost R10) | 1 |  |  |  |  |  | 170 |
| radio | 1 | 15 |  | 3 | 7 | 7 | 45 |
| coffee grinder | 1 | 107 |  | 0.02 | 7 | 7 | 1.8 |
|  |  |  |  |  |  |  | AC |
|  |  |  |  |  |  |  | Whr/Day |
|  |  |  |  |  |  |  | 607 |

## Sizing the System

| Note: Inverter for ranchhouse is undersized for full load. It is limited to 2500W, 275A |
| --- |
| A larger inverter would likely require changing system voltage to 24 or 48V. |
| Inverter Sizing Worksheet |
|  | Constraint | Site | AC Total Watts ÷ | DC system Voltage = | Max DC Amps Continuous |
|  | Summer | Ranch house + cabin | 4320 | 12 | 360 |
|  | Winter | Ranch house + cabin | 3969 | 12 | 330.75 |
| Inverter | Trace SW 2512 |  |  |  |  |
| Efficiency | 94% |  |  |  |  |
|  | Summer | Longhouse | 544 | 12 | 45.33 |
| Inverter |  |  |  |  |  |
| Efficiency |  |  |  |  |  |
|  | Winter | Longhouse | 544 | 12 | 45.33 |
| Inverter | InverterL Xantrex DR 1512 (1500 W) |  |  |  |  |
| Efficiency | 94% |  |  |  |  |

Battery Sizing

| Site | Ranchhouse/C. Cabin | Voltage |  | 6 |
| --- | --- | --- | --- | --- |
| Constraint | Winter | Ahr Capacity |  | 375 |
| Battery | Interstate UL-16 | Days of Autonomy = |  | 5 |
|  |  | Trace SW 2512, efficiency = | 0.94 |
|  |  | Discharge Limit = |  | 0.6 |
| AC Ave Daily Load ÷ | Inverter Efficiency + | DC Average Daily Load ÷ | DC System Voltage = | Ave Amp Hrs/Day |
| 2009.00 | 0.94 | 552.00 | 12.00 | 224.10 |
| Ave Amp Hrs/Day × | Days of Autonomy ÷ | Discharge Limit ÷ | Battery AH Capacity = | Batteries in Parallel |
| 224.10 | 5.00 | 0.60 | 375.00 | 4.98 |
| DC System Voltage ÷ | Battery Voltage = | Batteries in Series × | Batteries in Parallel = | Total Batteries |
| 12.00 | 6.00 | 2.00 | 4.98 | 9.96 |

Array Sizing Worksheet

| Ranchhouse - May |
| --- |
| Site | Ranchhouse |  |  |
| Seasonal Load | Winter |  |  |
| Design Month | May |  |  |
| Module | Evergreen EC-115 |  |  |
| Avg Amp-hrs/day ÷ | Battery efficiency ÷ | Peak Sun Hrs/day = | Peak Array Amps |  |
| 37.33 | 0.8 | 4.25 | 10.97 |  |
| Peak array amps ÷ | Peak Amps/module = | Modules in Parallel | Module Short Circuit Current |  |
| 10.97935881 | 6.65 | 1.65 | 7.26 |  |
| DC System Voltage ÷ | Nominal Module Volts = | Modules in Series * | Modules in parallel = | Total modules |
| 72 | 12 | 6 | 2 | 12 |
| Longhouse - Apr |
| Site | Longhouse |  |  |
| Seasonal Load | Winter |  |  |
| Design Month | April |  |  |
| Module | Siemans SP75 |  |  |
| Avg Amp-hrs/day ÷ | Battery efficiency ÷ | Peak Sun Hrs/day = | Peak Array Amps |  |
| 33.5 | 0.8 | 3.10 | 13.47 |  |
| Peak array amps ÷ | Peak Amps/module = | Modules in Parallel | Module Short Circuit Current |  |
| 13.468 | 4.7 | 2.87 | 4.8 |  |
| DC System Voltage ÷ | Nominal Module Volts = | Modules in Series * | Modules in parrallel = | Total modules |
| 24 | 12 | 2 | 3 | 6 |
| Longhouse – Sep |
| Site | Longhouse |  |  |
| Seasonal Load | Summer |  |  |
| Design Month | September |  |  |
| Module | Siemans SP75 |  |  |
| Avg Amp-hrs/day ÷ | Battery efficiency ÷ | Peak Sun Hrs/day = | Peak Array Amps |  |
| 62.5 | 0.8 | 4.44 | 17.60 |  |
| Peak array amps ÷ | Peak Amps/module = | Modules in Parallel | Module Short Circuit Current |  |
| 17.60 | 4.7 | 3.74 | 4.8 |  |
| DC System Voltage ÷ | Nominal Module Volts = | Modules in Series * | Modules in parallel = | Total modules |
| 24 | 12 | 2 | 4 | 8 |

Controller Sizing Worksheet

| Ranchhouse |  |  |  |
| --- | --- | --- | --- |
| Site | Ranchhouse |  |  |
| Seasonal Load | Summer |  |  |
| Module | Evergreen EC-115 |  |  |
| Module Short Circuit Current * | Modules in Parallel * | 1.25 = | Array Short Circuit Amps | Controller Array Amps |
| 7.26 | 2 | 1.25 | 18.15 | 100 |
| DC Total Connected Watts ÷ | DC System Voltage = | Maximum DC Load Amps | Controller Load Amps |  |
| 66 | 12 | 5.5 | 100 |  |
| Longhouse |  |  |  |
| Site | Longhouse |  |  |
| Seasonal Load | Summer |  |  |
| Module | Siemens SP75 |  |  |
| Module Short Circuit Current * | Modules in Parallel * | 1.25 = | Array Short Circuit Amps | Controller Array Amps |
| 4.8 | 3 | 1.25 | 18 | 50 |
| DC Total Connected Watts ÷ | DC System Voltage = | Maximum DC Load Amps | Controller Load Amps |  |
| 25 | 12 | 2.08 | 3 |  |

Wire Sizing Worksheet

| Ranchhouse |  |  |  |  |
| --- | --- | --- | --- | --- |
| PV Combiner to Controller |  |  |  |  |
| A. NEC Requirement |  |  |  |  |  |
| Isc of modules x | # of modules in parallel = | Total Amps | x 1.25 | x 1.25 = | NEC required |
| 7.26 | 1 | 7.26 | 9.07 | 11.34 | 11.34 |
| Amperage satisfying NEC = | 11.34 | Wire size from Table 9-4 = | # 14 AWG |  |  |
| B. Voltage Drop Requirements |  |  |  |  |
| System voltage = | 72 | Total Amps = | 7.26 |  |  |
| One Way Distance = | 340 | Voltage drop (%) = | 5 |  |  |
| VDI | 6.86 |  |  |  |  |
| Wire size from voltage drop tables (Tables 9-5 through 9-10) or VDI = | 8 # AWG |  |  |
| Is this equal or greater than the size wire needed for safety? | no |  |  |
| If yes, then the answer is E14, if no use wire size from A. | 8 # AWG |  |  |
| Controller to Battery |  |  |  |  |  |
| A. NEC Requirement |  |  |  |  |  |
| Isc of modules x | # of modules in parallel = | Total Amps | x 1.25 | x 1.25 = | NEC required |
| 7.26 | 12 | 87.12 | 108.9 | 136.12 | 136.12 |
| Amperage satisfying NEC = | 136.12 | Wire size from Table 9-4 = | 2/0 gauge |  |  |
| B. Voltage Drop Requirements |  |  |  |  |
| System voltage = | 12 | Total Amps = | 87.12 |  |  |
| One Way Distance = | 6 | Voltage drop (%) = | 5 |  |  |
| VDI | 8.71 |  |  |  |  |
| Wire size from voltage drop tables (Tables 9-5 through 9-10) = | # 6 AWG |  |  |
| Is this equal or greater than the size wire needed for safety? | yes |  |  |
| If yes, then the answer is E14, if no use wire size from A. | 2/0 gauge |  |  |
| Battery to Inverter |  |  |  |  |
| A. NEC Requirement |  |  |  |  |
| Inverter rated Watts ÷ | Inverter Efficiency ÷ | DC System (lowest operating) voltage = | Inverter Total Amps | x 1.25 = | NEC required |
| 2500 | 0.94 | 12 | 221.63 | 277.03 | 277.03 |
| Amperage satisfying NEC = | 277.04 | Wire size from Table 9-4 = | 3/0 Single Conductor |  |  |
| B. Voltage Drop Requirements |  |  |  |  |
| System voltage = | 12 | Total Amps = | 221.63 |  |  |
| One Way Distance = | 4 | Voltage drop (%) = | 5 |  |  |
| Wire size from voltage drop tables (Tables 9-5 thourgh 9-10) = | N/A |  |  |
| Is this equal or greater than the size wire needed for safety? |  |  |  |
| If yes, then the answer is E14, if no use wire size from A. |

| Wiring Worksheet: Longhouse |
| --- |
| PV Combiner to Controller |  |  |  |  |
| A. NEC Requirement |  |  |  |  |
| Isc of modules x | # of modules in parallel = | Total Amps | x 1.25 | x 1.25 = | NEC required |
| 4.8 | 4 | 19.2 | 24 | 30 | 30 |
| Amperage satisfying NEC = | 30 | Wire size from Table 9-4 = | #10 AWG |  |  |
| B. Voltage Drop Requirements |  |  |  |  |
| System voltage = | 24 | Total Amps = | 19.2 |  |  |
| One Way Distance = | 30 | Voltage drop (%) = | 5 |  |  |
| Wire size from voltage drop tables (Tables 9-5 thourgh 9-10) = | # 10 AWG |  |  |
| Is this equal or greater than the size wire needed for safety? | yes |  |  |
| If yes, then the answer is E14, if no use wire size from A. | # 10 AWG |  |  |
| Controller to Battery |  |  |  |  |
| A. NEC Requirement |  |  |  |  |  |
| Isc of modules x | # of modules in parallel = | Total Amps | x 1.25 | x 1.25 = | NEC required |
| 4.8 | 8 | 38.4 | 48 | 60 | 60 |
| Amperage satisfying NEC = | 60 | Wire size from Table 9-4 = | # 8 AWG |  |  |
| B. Voltage Drop Requirements |
| System voltage = | 12 | Total Amps = | 38.4 |  |  |
| One Way Distance = | 6 | Voltage drop (%) = | 5 |  |  |
| Wire size from voltage drop tables (Tables 9-5 thourgh 9-10) = | # 10 AWG |  |  |
| Is this equal or greater than the size wire needed for safety? | No |  |  |
| If yes, then the answer is E14, if no use wire size from A. | # 8 AWG |  |  |
| Battery to Inverter |  |  |  |  |
| A. NEC Requirement |  |  |  |  |
| Inverter rated Watts ÷ | Inverter Efficiency ÷ | DC System (lowest operating) voltage = | Inverter Total Amps | x 1.25 = | NEC required |
| 1500 | 0.94 | 12 | 132.98 | 166.22 | 166.22 |
| Amperage satisfying NEC = | 166.22 | Wire size from Table 9-4 = | 1/0 Single Conductors THW |  |  |
| B. Voltage Drop Requirements |
| System voltage = | 12 | Total Amps = | 132.98 |  |  |
| One Way Distance = | 4 | Voltage drop (%) = | 5 |  |  |
| Wire size from voltage drop tables (Tables 9-5 thourgh 9-10) = | # 4 AWG |  |  |
| Is this equal or greater than the size wire needed for safety? | No |  |  |
| If yes, then the answer is E14, if no use wire size from A. | 1/0 Single Conductors THW |

## Micro-hydro calculations

Gross Power:

Maximum velocity with no losses:

Find minimum pipe area for 150gpm:

Find minimum pipe diameter:

Max pressure without friction losses:

Friction Losses

218 feet of 3 inch schedule 40 pvc

3 X 3 inch 45 elbows head loss is equivalent to 4 feet of pipe

1 X 3 inch PVC gate valve 1.1 feet per inch diameter pipe

Net Power, assuming 5.38 ft head loss, 40% efficient turbine and generator

Wire sizing for micro-hydro runs to ranch house and long house:

Resistance is proportional to wire length and inversely proportional to wire area:

Furthermore,

Where cross-sectional area, A =

Rearranging and substituting,

Since we want Rr to equal Rl, .  From maps,

Lr is estimated to be 930 ft and Ll is estimated to be 315 ft.

Therefore, . Since a 6 gauge wire already exists between generator shed and ranch house, we assumed 6 gauge for the entire run.  The diameter of 6 gauge copper wire is 0.162 in.

The diameter of the other wire should therefore be 0.095 in, which leads to a specification of 11 gauge wire.  This analysis is confirmed by the estimated resistance per 1000 ft: 0.3951 for 6 gauge, and 1.26 ohms for 11 gauge.  (0.3951 * 993 = 392; 1.26 * 315 = 397)

http://www.powerstream.com/Wire_Size.htm

## Breakdown of Costs

Note: Blue indicates wire prices included in life cycle cost calculations.

Phase 1 Ranch House Alternative 1

| Equipment Costs |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Company | Description | Quantity Owned | Quantity to Buy | Length (ft) | Costs Each ($) | Capital Cost ($) | Life Time |
| Panels (i) | Evergreen EC-115 |  | 10 | 2 |  | 618.00 | 7416.00 | 30 |
| Copper Wires (b) | Industrial Electric | 8 gauge | This looks too low, don’t use! | 4 | 340 | 0.38 | 516.80 | 30 |
| Aluminum wires (a) | Industrial Electric | 6 gauge | Use this! | 4 | 340 | 0.73 | 992.80 | 30 |
| Disconnect (j) | Perfect Power | sloblo | 0 | 1 |  | 15.21 | 15.21 | 30 |
| Controller (c) | 1 Outback MX-60 |  | 1 | 1 |  | 649.00 | 649.00 | 10 |
| Copper Wires (b) | Industrial Electric | 2/0 gauge | 1 |  | 6 | 1.45 | 8.70 | 30 |
| Aluminum wires (a) | Industrial Electric | 8 gauge | 2 |  | 6 | 1.30 | 15.60 | 30 |
| Batteries (p) | 6 interstate UL16 |  |  | 10 |  | 199.95 | 1999.50 | 7-10 |
| Generator (m) | Honda |  | 1 |  |  | 2681.95 | 2681.95 | 15 |
| Gas (h) |  |  |  | 124 |  | 2.93 |  | 30 |
| Copper Wires (a) | Industrial Electric | 3/0 # (4/0 in stock) | 1 | 4 |  | 8.02 | 32.08 |  |
| Inverter (e) | Trace SW 2512 |  | 1 |  |  |  | 1299.00 | 10 |
| Disconnect (l) | Outback | PS2DC-175 |  | 1 |  | 375 | 375.00 | 30 |
| Ground Wire (a) | Industrial Electric | Aluminum # 4 AWG |  | 1 | 340 | 0.90 | 306.00 |  |
| All Wires |  |  |  |  |  |  | 863.58 |  |
| Capital Costs |  |  |  |  |  |  | 12892.29 |  |
| Total for comparison |  |  |  |  |  |  | 6712.29 |  |
| Longhouse Alternative 1 |
| Equipment Costs |  |  |  |  |  |  |  |  |
| Item | Company | Description | Quantity Owned | Quantity to Buy | Length (ft) | Costs Each ($) | Capital Cost ($) | Life Time |
| Panels (h) | 4 Siemens sp75 |  | 4 |  |  | 375.00 | 1500.00 | 30 |
| Panels (g) | 2 BP solar 380 |  | 4 |  |  | 457.00 | 1828.00 | 30 |
| Panels (q) | 2 Sharp 80 W |  |  | 2 |  | 479.16 | 958.32 | 30 |
| Copper Wires (b) | Industrial Electric | 10 gauge |  | 2 | 30 | 0.39 | 23.40 | 30 |
| Aluminum wires (a) | Industrial Electric | 8 gauge |  | 2 | 30 | 1.30 | 78.00 | 30 |
| Disconnect (j) | Perfect power | sloblo | 0 | 1 |  | 15.21 | 15.21 | 30 |
| Controller (c) | Xantrex C-60 |  | 0 | 1 |  | 167.16 | 167.16 | 10 |
| Copper Wires (a) | Industrial Electric | 8 gauge |  | 1 | 6 | 1.20 | 7.20 | 30 |
| Aluminum wires (a) | Industrial Electric | 6 gauge |  | 1 | 6 | 0.95 | 5.70 | 30 |
| Batteries (p) | 6 interstate UL16 |  | 6 |  |  | 199.95 | 1199.70 | 7-10 |
| Copper Wires (b) | Industrial Electric | 1/0 s c 4 feet *2 | 1 |  | 8 | 4.87 | 38.96 |  |
| Inverter (d) | Trace SW 1512 |  | 1 |  |  |  | 799.00 | 10 |
| Disconnect (l) | Outback | PS2DC-100 | 0 | 1 |  | 325.00 | 325.00 | 30 |
| All Wires |  |  |  |  |  |  | 69.56 |  |
| Total Capital |  |  |  |  |  |  | 7343.79 |  |
| Total for Comparison |  |  |  |  |  |  | 2816.09 |  |

Phase 1: Ranch House Alternative 2

| Equipment Costs |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Company | Description | Quantity Owned | Quantity to Buy | Length (ft) | Costs Each ($) | Capital Cost ($) | Life Time |
| Panels (i) | Evergreen EC-115 |  | 10 |  |  | 618.00 | 6,180.00 | 30 |
| Copper Wires (b) | Industrial Electric | 6 gauge |  | 4 | 340 | 0.97 | 1,319.20 | 30 |
| Aluminum wires (a) | Industrial Electric | 4 gauge |  | 4 | 340 | 0.90 | 1,224.00 | 30 |
| Disconnect (j) | Perfect Power | sloblo | 0 | 1 |  | 15.21 | 15.21 | 30 |
| Controller (c) | 1 Outback MX-60 |  | 1 | 1 |  | 649.00 | 1,298.00 | 30 |
| Copper Wires (b) | Industrial Electric | 2 gauge | 2 |  | 6 | 3.09 | 37.08 | 30 |
| Aluminum wires (a) | Industrial Electric | 8 gauge | 2 |  | 6 | 1.30 | 15.60 | 30 |
| Batteries (p) | 6 interstate UL16 |  |  | 10 |  | 199.95 | 1,999.50 | 7-10 |
| Generator (m) | Honda |  | 1 |  |  | 2681.95 | 2,681.95 | 15 |
| Gas (h) |  |  |  | 156 |  | 2.93 | 457.08 |  |
| Copper Wires (a) | Industrial Electric | 3/0 # (4/0 in stock) | 1 | 4 |  | 8.02 | 32.08 |  |
| Inverter (e) | Trace SW 2512 |  | 1 |  |  |  | 1,299.00 | 10 |
| Disconnect (l) |  | throws |  | 2 |  | 325 | 650.00 | 30 |
| Ground Wire (a) | Industrial Electric | Aluminum # 4 AWG |  | 1 | 340 | 0.90 | 306.00 | 30 |
| All Wires |  |  |  |  |  |  | 1,694.36 |  |
| Capital Costs |  |  |  |  |  |  | 13,136.07 |  |
| Total for comparison |  |  |  |  |  |  | 5,008.07 |  |
| Longhouse Alternative 2 |
| Equipment Costs |  |  |  |  |  |  |  |  |
| Item | Company | Description | Quantity Owned | Quantity to Buy | Length (ft) | Costs Each ($) | Capital Cost ($) | Life Time |
| Panels (h) | 4 Siemens sp75 |  | 4 |  |  | 375.00 | 1,500.00 | 30 |
| Panels (g) | 2 BP solar 380 |  | 2 |  |  | 457.00 | 914.00 | 30 |
| Copper Wires (b) | Industrial Electric | 10 gauge |  | 2 | 30 | 0.39 | 23.40 | 30 |
| Aluminum wires (a) | Industrial Electric | 8 gauge |  | 2 | 30 | 0.95 | 57.00 | 30 |
| Disconnect (j) | Perfect Power | sloblo | 0 | 1 |  | 15.21 | 15.21 | 30 |
| Controller (r) | Xantrex C-60 |  | 0 | 1 |  | 167.16 | 167.16 | 10 |
| Copper Wires (a) | Industrial Electric | 8 gauge |  | 1 | 6 | 1.20 | 7.20 | 30 |
| Aluminum wires (a) | Industrial Electric | 6 gauge |  | 1 | 6 | 0.95 | 5.70 | 30 |
| Batteries | 6 interstate UL16 |  | 6 |  |  | 199.95 | 1,199.70 | 7-10 |
| Copper Wires (b) | Industrial Electric | 1/0 s c 4 feet *2 | 1 |  | 8 | 4.87 | 38.96 | 30 |
| Inverter (d) | Trace SW 1512 |  | 1 |  |  |  | 799.00 | 10 |
| Disconnect (l) |  | throws |  | 1 |  | 325.00 | 325.00 | 30 |
| All Wires |  |  |  |  |  |  | 69.56 |  |
| Total Capital |  |  |  |  |  |  | 5,471.47 |  |
| Total for Comparison |  |  |  |  |  |  | 1,857.77 |  |

Phase II: Micro-hydro

| Equipment Costs |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Company | Description | Quantity to Buy | Length (ft) | Costs Each ($) | Capital Cost ($) | Life Time |
| 600 W Pelton Wheel with Rectifier (f) | Hi-Power Hydro |  | 1 |  | 2,500.00 | 2,500.00 | 15 |
| 2nd Transformer/Rectifier (k) | Hi-Power Hydro |  | 1 |  | 50.00 | 50.00 | 15 |
| Shunt Controller (f) | Hi-Power Hydro |  | 2 |  | 199.00 | 398.00 | 10 |
| Diversion Load (f) | Hi-Power Hydro |  | 2 |  | 225.00 | 450.00 | 10 |
| Pipe Size (n) |  | 3" Schedule 40 PVC |  | 218 | 21.55/9 | 538.75 | 30 |
| Wires to RH (a) | Industrial Electric | Copper #6 | 2 | 793 | 0.97 | 1538.42 | 30 |
| Wires to LH (a) | Industrial Electric | Copper #10 | 2 | 315 | 0.38 | 239.40 | 30 |
| Total |  |  |  |  |  | 5,980.35 |  |

## Sources for prices

| Item | Sources |
| --- | --- |
| a) | Industrial Electric (phone call) |
| b) | http://store.solar-electric.com/hardware---wire.html |
| c) | http://outbackpower.com/PriceList.htm |
| d) | http://www.wholesalesolar.com/products.folder/inverter-folder/DR1512.html |
| e) | http://store.wmjmarine.com/rv2512.htm |
| f) | http://www.hipowerhydro.com/ |
| g) | http://www.solar4power.com/store/010-040-bp.htm |
| h) | http://www.bitterrootsolar.com/solar/sp75.htm |
| i) | http://www.sierrasolar.com/manufacturers.php?manufacturer_id=97 |
| j) | http://perfectpowernetwork.com/Product/1068/T1,0013,0080/Assorted-Fuses.htm |
| k) | http://www.toroid.com/standard_transformers/rectifier_transformers/rectifier_transformers_mult.htm |
| l) | http://www.wholesalesolar.com/products.folder/disconnect-folder/Outback.disc.folder/outback.disconnects.html |
| m) | http://www.hondapowerequipment.com |
| n) | http://www.coleparmer.com/catalog/product_index.asp?cls=42584 |
| o) | http://www.backwoodssolar.com/Catalogpages2/pvmount2.htm#Universal%20Post%20Mounts |
| p) | Interstate Batterires, Eureka (phone call) |
| q) | http://store.altenergystore.com/Solar-Electric-Panels/51-to-99-Watt-Solar-Panels/Sharp-NE-80EJE-80W-12V-Solar-Panel/p1077/ |
| r) | http://store.solar-electric.com/tracc6060amp.html |